## Slide 1: Bridgeland Water System
Harris county mud 418, 419, & 489
September 13, 2021

## Slide 2: Agenda
Background
  Drought Contingency Plan defined
  Water Modeling
  Plant design
Initial Water Quality Challenges
  Split System origination
  WQT testing before/after
  Split System
  WQT results
  Current Water Supply Capabilities
Current Water Quality Challenges
  Comprehensive Potable water production/metering
  Most recent data – Plant 1/2
  STP Data
  STP & Flushing irrigation breakdown
  North Water Plant Pressure readings 08/30-09/10
  South Water Plant Pressure readings 08/30-09/10
  Theories
  Solutions

## Slide 3: Drought Contingency Plan
https://texreg.sos.state.tx.us/public/readtac$ext.TacPage?sl=R&app=9&p_dir=&p_rloc=&p_tloc=&p_ploc=&pg=1&p_tac=&ti=30&pt=1&ch=288&rl=20
A drought contingency plan for a retail public water supplier, where applicable, must include the following minimum elements.
(1) Minimum requirements. Drought contingency plans must include the following minimum elements.
(A) Preparation of the plan shall include provisions to actively inform the public and affirmatively provide opportunity for public input. Such acts may include, but are not limited to, having a public meeting at a time and location convenient to the public and providing written notice to the public concerning the proposed plan and meeting.
(B) Provisions shall be made for a program of continuing public education and information regarding the drought contingency plan.
(C) The drought contingency plan must document coordination with the regional water planning groups for the service area of the retail public water supplier to ensure consistency with the appropriate approved regional water plans.
(D) The drought contingency plan must include a description of the information to be monitored by the water supplier, and specific criteria for the initiation and termination of drought response stages, accompanied by an explanation of the rationale or basis for such triggering criteria.
(E) The drought contingency plan must include drought or emergency response stages providing for the implementation of measures in response to at least the following situations:
(i) reduction in available water supply up to a repeat of the drought of record;
(ii) water production or distribution system limitations;
(iii) supply source contamination; or
(iv) system outage due to the failure or damage of major water system components (e.g., pumps).
(F) The drought contingency plan must include specific, quantified targets for water use reductions to be achieved during periods of water shortage and drought. The entity preparing the plan shall establish the targets. The goals established by the entity under this subparagraph are not enforceable.
(G) The drought contingency plan must include the specific water supply or water demand management measures to be implemented during each stage of the plan including, but not limited to, the following:

## Slide 4: DCP Summary
Level1
  Trigger - Well Run times/RWA Supply is equivalent to 16 hours per day
  Release
Level 2
  Trigger - Well Run times/RWA Supply is equivalent to 18 hours per day
  Release
Level
  Trigger - Well Run times/RWA Supply is equivalent to 20 hours per day
  Release

## Slide 5: WATER MODELING

## Slide 6: WATER PLANT #1
WATER PLANT #2
"ULTIMATE “WATER PLANT DESIGN

## Slide 7: Split System Origination
Water Plant #1 (Water well 1&2; WHCRWA)
  Traditionally disinfected with Chlorine
  Aesthetically pleasing; inexpensive to produce
Subsidence created the need to move to surface water
West Harris County Regional Water Authority (WHCRWA)
Surface Water
  Can not treat with chlorine. (produces THM)
  Only can use Chloramines
  WATER PLANT #2 (water well #3)
    Well #3 began producing water with Iron Reducing Bacteria (IRB)
    The water with the IEB began reacting with the water from WP1 and creating water quality issues in entire water system.
    The only solution was to flush water nonstop to reduce reaction; not a long-term fix
    The idea was to isolate the systems into North and South
      North:WHCRWA and 2 wells
      South: Wells only

## Slide 8: “Split” System
NORTH SYSTEM
SOUTH
SYSTEM

## Slide 9: HC419 WQT 201908
HC419 WQT 202108

## Slide 10: “CURRENT” WATER PLANT CAPABILITIES

## Slide 11: WHCRWA/BRIDGELAND SUMMARY
HC MUD 418 has a water supply commitment with the WHCRWA in the amount of 2.1 MGD, provided the water is available and we do not have any type of emergency condition. Because of this commitment, the Bridgeland metering station has been labeled a priority site, which means that the WHCRWA operations team will make every effort to supply the district with their contracted flow, and the MUD operator is first to be notified of any condition affecting the operation of the Authority.
Typically, we would set the metering station valves to that flow in gallons per minute, which is just under 1500 GPM, and tell the operator to lower the well setpoint and take more surface water. However, after extensive talks with Jeremy over the summer seasons, a set GPM is not enough to keep up with the MUD’s morning and overnight demand. We have seen this many times over the years, with both wells running and 3000 GPM of surface water supplied, the EST and GST levels at Water Plant #1 are still dropping at 6 AM.
The WHCRWA operations team has a specific plan in place for HC MUD 418, where the metering station valves are set up to run at their maximum capacity of 2500 GPM on average for peak summer hours up to 3000 GPM, and any flow reductions needed on our side would be done during periods of lower demand after the MUD receives their daily contracted flow.

## Slide 12: Comprehensive Potable water production/metering

## Slide 13: Most recent data – Plant 1

## Slide 14: Most recent data – Water Plant #2

## Slide 15: STP Data

## Slide 16: STP & Flushing irrigation breakdown
Is flushing causing our water issues?
  79.821M is what the Bridgeland pumped and received from WHCRWA in July 2021
  2.376M was flushed in the community during July 2021
  Roughly speaking that is 2.976% per month is used for flushing
How much water goes to the sanitary waste?
  79.821M is what the Bridgeland pumped and received from WHCRWA in July 2021
  35.836M was measured at the STP. (We averaged 1.156M per day at STP)
  Roughly 44.89% of the pumped/received water is treated at the STP
How much are we using to irrigate and sanitary waste?
  38.282M, or 47.95% is used to flushing and STP
How much are we using to irrigate?
  41.528M or 52.055 is used for residential irrigation

## Slide 17: North Water Plant Pressure readings 08/30-09/10
MONDAY
08/30/2021
6:00am
WEDNESDAY
09/01/2021
6:00am
SUNDAY
09/05/2021
6:00am
MONDAY
09/06/2021
6:00am
WEDSNESDAY
09/08/2021
6:00am
FRIDAY
09/10/2021
6:00am
THURSDAY
09/09/2021
6:00am

## Slide 18: South Water Plant Pressure readings 08/30-09/10
MONDAY
08/30/2021
6:00am
WEDNESDAY
09/01/2021
7:00am

## Slide 19: Theories
Residents are replanting damaged vegetation from URI.
Most irrigation systems are “preset” by irrigation companies to run MWF in the early morning.
Many families are getting ready for work and school in the early morning.
Some curbs in Bridgeland have black algae growing on sides or green algae growing on sidewalks; signs over overwatering.
Conclusion: There is a significant amount of potable usage specifically from 4:00am-8:00am MWF

## Slide 20: Solutions
  Install pressure sensors at strategic points around community too monitor system pressure
  Convert 300 connections from North to South
  Bring Well #4 online (WP2)
  Convert 300 more connections from North to South
  Bring Inframark into the social media circles to help residents understand facts, including Facebook Live sessions
  Modify DCP and communicate to include designated watering day and times
  Engage “Water Wise” type program to assist residents on how to properly water including:
    Irrigation programming videos/assistance
    Online water use calculators; Aeration of yards
    September 15th
    September 25th
    ASAP(Waiting on TCEQ)
    October 15th
    ASAP
    December 1
    ASAP